| HYDROSTATIC PRESSURE TEST & LEAKAGE TEST REPORT EXTERNAL PIPELINE | Form QT4(a) |
| --- | --- |
|  | Page 1 of 2 |

| Name of Development | : |  |
| --- | --- | --- |
| Project Reference No. | : |  |

- Pressure Test

| Testing Date | : |  | Time : |  |
| --- | --- | --- | --- | --- |
| Preperations for Test | : | Satisfactory / Not Satisfactory |  |  |

| Description Of Pipeline | Max Lenght | (√) |  | Pipe Material | Pressure Test (Bar) | (iii) Leakage Test (Bar) |
| --- | --- | --- | --- | --- | --- | --- |
| Trunk Main | 3 km |  |  | HDPE (PN12.5) | 12.0 | 8.0 |
| Reticulation Pipe | 2km |  |  | Steel | 15.0 | 12.0 |
|  |  |  |  | Ductile Iron | 15.0 | 12.0 |
|  |  |  |  | ABS (CL 12) | 12.0 | 8.0 |

| Pipe Material | Pipe Location |  | (i) Internal Pipe Dia. (mm)- | (ii) Pipe Lenght (m) | Initial Specified Pressure (Bar) | Final Pressure after 10mins / 1 hour (Bar)* | Result |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | From; Pt./ CH./ Node | To; Pt./ CH./ Node |  |  |  |  | Pass √ | Fail X |

* Steel Pipe : The pressure must stand at 15 Bar for 10 minutes with no allowable drop.

* HDPE Pipe : The pressure must stand at 12 Bar for 1 hour with the allowable drop of 0.1bar (max).

- Leakage Test – External Pipeline & Main Pipe

| Testing Date | : |  | Time : |  |
| --- | --- | --- | --- | --- |
| Preperations for Test | : | Satisfactory / Not Satisfactory |  |  |

|  |  |  | (i) | (ii) |  | (iii) |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Allowable Leakage For Steel Pipe | = | 0.34 liter x | internal pipe dia. (mm) x | pipe length (m) x | total test duration (hour) x | leakage test (bar) | (Liters) |
|  |  | 10 x 1000 x 24 hr x 1 bar |  |  |  |  |  |

| Pipe Location |  | (iv) Allowable Leakage* | Initial Specified Pressure (Bar ) | Final Pressure (Bar) | Total make-up water (liter) | Result |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| From; Pt./ CH./ Node | To; Pt./ CH./ Node |  |  |  |  | Pass √ | Fail X |

* Steel Pipe : The pressure must stand at 12 Bar for 24 hrs with the alowable drop within the specified rate

* HDPE Pipe : The pressure must stand at 8 Bar for 2 hrs with no allowable drop

| HYDROSTATIC PRESSURE TEST & LEAKAGE TEST REPORT EXTERNAL PIPELINE | Form QT4(a) |
| --- | --- |
|  | Page 2 of 2 |

Note: The pressure chart recorder result shall be attached with this report.

| Checked By |  |  |  |
| --- | --- | --- | --- |
| Name | : |  |  |
| Firm CP Registration No | : : |  |  |
| NRIC. No. | : |  |  |
| Date : |  | Signature of Competent Person |  |
| Witnessed By |  |  |  |
| Name | : |  |  |
| Staff No | : |  |  |
|  |  | Signature of AIR SELANGOR; Executives/ Technician Regional Development Unit |  |

Date                           :