| WATER TIGHTNESS TEST REPORT FOR RESERVOIR/ SUCTION CISTERN | Form QT5 |
| --- | --- |
|  | Page 1 of 2 |

| Name of Development | : |  |
| --- | --- | --- |
|  | : |  |
|  | : |  |
| Project Reference No. | : |  |

- Watertightness Test

| Testing Date | : |  | Time : |  |
| --- | --- | --- | --- | --- |
| Type of Reservoir | : |  |  |  |
| Reservoir ID | : |  |  |  |
| Reservoir Capacity | : |  |  |  |

| A. | Reduced water level (in reservoir) |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | i) Initial water level | mm |  | Date: |  | Time: |  |
|  | ii) Final water level | mm |  | Date: |  | Time: |  |
| B. | Evaporation (in tray)* |  |  |  |  |  |  |
|  | iii) Initial water level | mm |  | Date: |  | Time: |  |
|  | iv) Final water level | mm |  | Date: |  | Time: |  |
|  | *Using tray size 0.4 sq.m containing not less than 75mm depth of water |  |  |  |  |  |  |

| (v) | Allowable Leakage | : | 1 x | Depth of water (mm) |
| --- | --- | --- | --- | --- |
|  |  |  | 2000 |  |

| Drop in water (After 72 hours) (mm) |  | Actual Leakage | Allowable Leakage (mm) | Result |  |
| --- | --- | --- | --- | --- | --- |
| level A (i-ii) | level B (i-ii) | level A - level B | (v) | Pass √ | Fail X |

Result:	Pass  = If; Actual Leakage < Allowable Leakage

Fail   = If; Actual Leakage > Allowable Leakage

Note:  a.		The procedure shall refer with the general principles in SPAN’s Uniform Technical Guidelines and in accordance with SYABAS’ Standard Specification For Pipe Laying Works First Edition: May 2007 requirements.

| WATER TIGHTNESS TEST REPORT FOR RESERVOIR/ SUCTION CISTERN | Form QT5 |
| --- | --- |
|  | Page 2 of 2 |

| Project Reference No. | : |  |
| --- | --- | --- |

| Checked By |  |  |  |
| --- | --- | --- | --- |
| Name | : |  |  |
| Firm CP Registration No | : : |  |  |
| NRIC. No. | : |  |  |
| Date : |  | Signature of Competent Person |  |
| Witnessed By |  |  |  |
| Name | : |  |  |
| Staff No | : |  |  |
|  |  | Signature of AIR SELANGOR; Executives/ Technician Regional Development Unit |  |

Date                           :